Barker Energy Center Project

PSCAD Dynamic Model Quality Testing

# Project Overview

Performed comprehensive PSCAD model dynamic compliance testing for Invenergy's proposed 461.232 MW Barker Energy Center project to validate whether the dynamic model satisfies requirements from the Unity grid operator. Built equivalent electromagnetic transient models for two synchronous machines connected through two main power transformers to the Cole 230 kV Substation and executed five critical test scenarios.

## Project Scope

| Client | Invenergy |
| --- | --- |
| Project | Barker Energy Center |
| System Capacity | 461.232 MW (2 synchronous machines) |
| Voltage Level | 230 kV (Cole Substation) |
| Transmission Line | 2.90-mile (15,312 ft) overhead line |
| Date | April 2026 |
| Software | PSCAD v5.0.2 |

## Key Responsibilities

- Built equivalent PSCAD model for two synchronous machines, two main power transformers (MPTs), and a 2.90-mile 230 kV overhead transmission line connected to the Cole Substation

- Implemented IEEE standard dynamic models provided by the manufacturer: GENROU generator, ESST4B excitation system, PSS2B power system stabilizer, and GGOV1 governor model

- Executed five MQT scenarios per Unity requirements: Flat Start, Bump Test (three-phase-to-ground fault at t=50s for 6 cycles), Exciter Voltage Reference Tests with and without PSS, and Governor Reference Test

- Tuned PSCAD model parameters to match as-built field system data for accurate representation of generator control behavior

- Validated model performance through post-processing analysis of active power, reactive power, and voltage responses at the point of interconnection (POI) and individual generator terminals

## Technical Analysis

Ran full dynamic compliance testing across all five MQT scenarios. The Flat Start Test confirmed clean initialization with no deviations. The Bump Test demonstrated fault ride-through capability with both machines maintaining synchronism during the 6-cycle three-phase fault. Voltage reference step tests at plus and minus 3 percent verified responsive excitation control, with PSS effectively damping oscillations. Governor reference testing confirmed smooth, non-oscillatory active power response, showing well-tuned control parameters ready for grid operator submission.

## System Configuration

- Generators: Two synchronous machines with full IEEE dynamic models (GENROU, ESST4B, PSS2B, GGOV1)

- Main Power Transformers: Two three-winding MPTs with corresponding impedances and ratings

- Transmission Line: 2.90-mile 230 kV overhead line to Cole 230 kV Substation

- Utility Source: Generic gencls voltage source at 230 kV with short-circuit MVA per Unity specification

- Control Systems: Full dynamic representation including voltage regulation, power system stabilization, and frequency control

## Test Results Summary

| Test Case | Result |
| --- | --- |
| Flat Start Test | Pass |
| Bump Test (Three-Phase Fault) | Pass |
| Exciter Voltage Reference Test (With PSS) | Pass |
| Exciter Voltage Reference Test (Without PSS) | Pass |
| Governor Reference Test | Pass |

## Technical Skills Demonstrated

- EMT Simulation: PSCAD electromagnetic transient modeling for synchronous machine systems

- Dynamic Models: GENROU, ESST4B, PSS2B, GGOV1 per IEEE standards

- Grid Compliance: Unity interconnection requirements for 230 kV systems

- Control Systems: Excitation control, governor control, power system stabilizer tuning

- Testing Standards: Model quality testing per utility specifications

## Deliverables

- Complete PSCAD dynamic model with validated initialization for Barker Energy Center

- PSCAD Dynamic Simulation Test Report documenting modeling methodology, system assumptions, test procedures, and comprehensive results

- Time-domain waveform plots for all five test scenarios at POI and individual generator terminals

- Complete parameter tables for generators, transformers, and transmission line

- PSCAD model files ready for Unity submission and interconnection studies

## Impact

Successfully demonstrated full compliance with Unity grid operator requirements, enabling Invenergy to proceed with interconnection approval for the 461.232 MW Barker Energy Center. All five MQT scenarios passed, confirming that the dynamic model accurately represents the generator control system and meets grid stability standards.