Grand View EGS I Project

PSCAD Dynamic Model Quality Testing

# Project Overview

Performed PSCAD model dynamic compliance testing for Invenergy's 265.88 MW Grand View EGS I project to validate grid interconnection compliance per Unity requirements. The system uses four synchronous machines connected through one main power transformer and four generator step-up transformers to the 230 kV Hemingway Substation via a 35-mile transmission line.

## Project Scope

| Client | Invenergy |
| --- | --- |
| Project | Grand View EGS I (Enhanced Geothermal System) |
| System Capacity | 265.88 MW (4 synchronous machines) |
| Voltage Levels | 230 kV / 69 kV |
| Transmission Lines | 35-mile 230 kV line; four 1-mile 69 kV collector lines |
| Substation | 230 kV Hemingway Substation |
| Date | April 2026 |
| Software | PSCAD v5.0.2 |

## Key Responsibilities

- Developed equivalent PSCAD model for four synchronous machines, one main power transformer (MPT), four generator step-up transformers (GSUs), a 35-mile 230 kV line, and four 1-mile 69 kV collector lines

- Implemented IEEE standard dynamic models: GENROU generator, AC7B excitation system with rotating exciter, PSS2B power system stabilizer, and TGOV1 steam turbine governor

- Executed five MQT scenarios per Unity requirements: Flat Start, Bump Test, Exciter Voltage Reference Tests with and without PSS, and Governor Reference Test

- Tuned PSCAD model parameters to match as-built field data for accurate representation of each generator control system

- Validated active power, reactive power, and voltage responses at POI and at each individual generator terminal

## Technical Analysis

The Flat Start Test confirmed clean initialization with no deviations across all four machines. The Bump Test demonstrated fault ride-through with all generators maintaining synchronism during the 6-cycle three-phase fault. Voltage reference step tests at plus and minus 3 percent verified responsive excitation control, with PSS damping oscillations effectively. Governor reference testing confirmed smooth active power response across all units, showing the model is ready for Unity submission.

## System Configuration

- Generators: Four synchronous machines with full IEEE dynamic models (GENROU, AC7B, PSS2B, TGOV1)

- Main Power Transformer: One three-winding MPT at 230 kV / 69 kV with corresponding impedances

- Generator Step-Up Transformers: Four two-winding GSUs at 69 kV

- Transmission Lines: One 35-mile 230 kV line and four 1-mile 69 kV collector circuits

- Utility Source: Generic gencls voltage source at 230 kV with Unity-defined short-circuit MVA

## Test Results Summary

| Test Case | Result |
| --- | --- |
| Flat Start Test | Pass |
| Bump Test (Three-Phase Fault) | Pass |
| Exciter Voltage Reference Test (With PSS) | Pass |
| Exciter Voltage Reference Test (Without PSS) | Pass |
| Governor Reference Test | Pass |

## Technical Skills Demonstrated

- EMT Simulation: PSCAD modeling for multi-machine geothermal systems

- Dynamic Models: GENROU, AC7B, PSS2B, TGOV1 per IEEE standards

- Grid Compliance: Unity requirements for 230 kV / 69 kV systems

- Multi-Machine Modeling: Four-generator synchronous system with shared MPT and individual GSUs

- Testing Standards: Model quality testing per utility specifications

## Deliverables

- Complete PSCAD dynamic model with validated initialization for all four generators

- PSCAD Dynamic Simulation Test Report documenting modeling methodology, assumptions, test procedures, and results

- Time-domain waveform plots for all five test scenarios at POI and each generator terminal

- PSCAD model files ready for Unity submission and interconnection studies

## Impact

Confirmed full compliance with Unity requirements for the 265.88 MW Grand View EGS I project. All five MQT scenarios passed, enabling Invenergy to advance the interconnection approval process for this four-unit enhanced geothermal facility.