Whispering Sands Energy Center Project

PSCAD Dynamic Model Quality Testing

# Project Overview

Performed PSCAD model dynamic compliance testing for Invenergy's 1,506.64 MW Whispering Sands Energy Center project to validate compliance with Unity grid operator requirements. The system consists of four synchronous machines connected through four main power transformers to the APS Hassayampa-N. Gila #2 (HANG2) 500 kV Substation via two short 0.1-mile transmission lines.

## Project Scope

| Client | Invenergy |
| --- | --- |
| Project | Whispering Sands Energy Center |
| System Capacity | 1,506.64 MW (4 synchronous machines) |
| Voltage Level | 500 kV (APS HANG2 Substation) |
| Transmission Lines | Two 0.1-mile (528 ft) overhead lines |
| Substation | APS Hassayampa-N. Gila #2 (HANG2) 500 kV |
| Date | April 2026 |
| Software | PSCAD v5.0.2 |

## Key Responsibilities

- Built equivalent PSCAD model for four synchronous machines, four three-winding main power transformers (MPTs), and two 0.1-mile 500 kV overhead lines to the APS HANG2 Substation

- Implemented IEEE standard dynamic models provided by the manufacturer: GENROU generator, ESST4B excitation system, PSS2B power system stabilizer, and GGOV1 governor

- Executed five MQT scenarios per Unity requirements: Flat Start, Bump Test, Exciter Voltage Reference Tests with and without PSS, and Governor Reference Test

- Tuned PSCAD model parameters to as-built field data for accurate representation of all four generator control systems at 500 kV

- Validated active power, reactive power, and voltage responses at POI and individual generator terminals

## Technical Analysis

All five MQT scenarios confirmed compliance for this large four-unit facility. The Flat Start showed clean initialization across all machines. The Bump Test verified fault ride-through with all four generators maintaining synchronism during the 6-cycle three-phase fault. Voltage reference step tests confirmed responsive excitation with effective PSS damping. Governor testing showed non-oscillatory active power response from all four units simultaneously, demonstrating well-coordinated control suitable for grid operator submission.

## System Configuration

- Generators: Four synchronous machines with full IEEE dynamic models (GENROU, ESST4B, PSS2B, GGOV1)

- Main Power Transformers: Four three-winding MPTs with corresponding impedances and ratings

- Transmission Lines: Two 0.1-mile 500 kV overhead lines to APS HANG2 Substation

- Utility Source: Generic gencls voltage source at 500 kV with Unity-defined short-circuit MVA

- Control Systems: Full dynamic representation including voltage regulation, power system stabilization, and frequency control for all four units

## Test Results Summary

| Test Case | Result |
| --- | --- |
| Flat Start Test | Pass |
| Bump Test (Three-Phase Fault) | Pass |
| Exciter Voltage Reference Test (With PSS) | Pass |
| Exciter Voltage Reference Test (Without PSS) | Pass |
| Governor Reference Test | Pass |

## Technical Skills Demonstrated

- EMT Simulation: PSCAD modeling for large four-unit synchronous generator facilities at 500 kV

- Dynamic Models: GENROU, ESST4B, PSS2B, GGOV1 per IEEE standards

- Grid Compliance: Unity requirements for 500 kV interconnection with APS HANG2 Substation

- Multi-Machine Modeling: Four-generator system with individual MPTs on a shared 500 kV bus

- Testing Standards: Model quality testing per utility specifications

## Deliverables

- Complete PSCAD dynamic model for Whispering Sands with validated initialization for all four generators

- PSCAD Dynamic Simulation Test Report documenting modeling methodology, assumptions, test procedures, and comprehensive results

- Time-domain waveform plots for all five test scenarios at POI and each generator terminal

- PSCAD model files ready for Unity submission and interconnection studies

## Impact

Confirmed full compliance with Unity requirements for the 1,506.64 MW Whispering Sands Energy Center. All five MQT scenarios passed, enabling Invenergy to proceed with interconnection approval for this large four-unit facility at the APS Hassayampa-N. Gila #2 500 kV Substation.